## Sheet1
Very Basic Harmonic Resonance and Voltage Rise Percent
Input Blue
Harmonic Resonance | Capacitors |  | Transformer |  | Impedance
Harmonic Order | kVAR |  | kVA |  | Z%
5.7505 | 5400 |  | 15000 |  | 8.4
Percent Voltage Rise
3.024%
Amps
Voltage Phase to Phase |  | Capacitors |  | Transformers
13080 |  | 238.3556 |  | 662.0989
| MicroFarad |  |  | Constant
| 83.7215 |  |  | 1.7321