## Sheet1
NOTE: THESE READING CAN ONLY BE TAKEN AT THE TRANSFORMER BEING RATED.
THREE PHASE TRANSFORMER ONLY
Input Blue
| IEEE C57.110 |  | Note: THESE READING COULD BE CONSERVATIVE USING
HARMONIC ORDERS OVER THE 19TH.
| Harmonic Order | Ipu | Ipu2 | h2 | Ipu2h2 | fh | fh2 | fh2
| 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 3 | 0.2356 | 0.055507 | 9 | 0.49957 | 0.2356 | 0.055507 | 0.49957
| 5 | 0.1182 | 0.013971 | 25 | 0.34928 | 0.1182 | 0.013971 | 0.34928
| 7 | 0.0438 | 0.0019184 | 49 | 0.094004 | 0.0438 | 0.0019184 | 0.094004
| 9 | 0.0142 | 0.00020164 | 81 | 0.016333 | 0.0142 | 0.00020164 | 0.016333
| 11 | 0.0182 | 0.00033124 | 121 | 0.04008 | 0.0182 | 0.00033124 | 0.04008
| 13 | 0.0069 | 4.761e-05 | 169 | 0.0080461 | 0.0069 | 4.761e-05 | 0.0080461
| 15 | 0.0022 | 4.84e-06 | 225 | 0.001089 | 0.0022 | 4.84e-06 | 0.001089
| 17 | 0.0038 | 1.444e-05 | 289 | 0.0041732 | 0.0038 | 1.444e-05 | 0.0041732
| 19 | 0.0072 | 5.184e-05 | 361 | 0.018714 | 0.0072 | 5.184e-05 | 0.018714
| 21 | 0.0018 | 3.24e-06 | 441 | 0.0014288 | 0.0018 | 3.24e-06 | 0.0014288
| 23 | 0.0075 | 5.625e-05 | 529 | 0.029756 | 0.0075 | 5.625e-05 | 0.029756
| 25 | 0.0022 | 4.84e-06 | 625 | 0.003025 | 0.0022 | 4.84e-06 | 0.003025
| 27 | 0 | 0 | 729 | 0 | 0 | 0 | 0
| 29 | 0 | 0 | 841 | 0 | 0 | 0 | 0
| 31 | 0 | 0 | 961 | 0 | 0 | 0 | 0
| 33 | 0 | 0 | 1089 | 0 | 0 | 0 | 0
| 35 | 0 | 0 | 1225 | 0 | 0 | 0 | 0
| 37 | 0 | 0 | 1369 | 0 | 0 | 0 | 0
| 39 | 0 | 0 | 1521 | 0 | 0 | 0 | 0
| 41 | 0 | 0 | 1681 | 0 | 0 | 0 | 0
| 43 | 0 | 0 | 1849 | 0 | 0 | 0 | 0
| 45 | 0 | 0 | 2025 | 0 | 0 | 0 | 0
| 47 | 0 | 0 | 2209 | 0 | 0 | 0 | 0
| 49 | 0 | 0 | 2401 | 0 | 0 | 0 | 0
| S | 0 | 1.0721 |  | 2.0655 |  | 1.0721 | 2.0655
Transformer kVA
eddy current |  | 10% |  | 150
Derating Factor |  | 95.48%
kVA
Transformer derated to: |  |  | 143.2237
If eddy currents losses are not known. Use the follow to calculate the derating.
Input Blue
|  | HV | LV |  |  | Power losses in watts @ 75C
| Voltages | 12000 | 480 |  |  | 3124
|  | DELTA |  | WYE
| DC Resistance | Ohms HV | Ohms LV | Ohms HV | Ohms LV
| of windings | 4.56 | 0.00411 | 0 | 0 | winding eddy-current loss in watts
|  | Calculated ohms due to resistance in series |  |  |  |  | 3000.237
|  | 1.0133 | 0.00091333 | 0 | 0
|  | HV amps | LV amps
|  | 7.2169 | 180.422
Winding eddy-current loss if turns ratio exceeds 4:1 and secondary current exceeds 1000 amps
188.3711
Winding eddy-current loss if turns ratio does not exceed 4:1 or secondary current does not exceed 1000 amps
161.4609
| Turns Ratio exceed 4:1 |  |  |  | Turns Ratio NOT exceed 4:1
| Derating Factor |  | 72.14% |  | Derating Factor |  | 72.15%
|  |  | kVA |  |  |  | kVA
| Transformer derated to: |  | 108.206 |  | Transformer derated to: |  | 108.2289