## Sheet1
| Voltage Unbalance |  |  |  |  | Current Unbalance
| Maximum deviation from average voltage divided by average voltage. |  |  |  |  | Maximum deviation from average current divided by average current.
INPUT BLUE
|  | Voltage Balance |  |  |  |  | Current Balance
|  | A | B | C |  |  | A | B | C
| 487 | ab |  |  |  | 33 | a
| 487 | ac |  |  |  | 37 | b
| 467 | cb |  |  |  | 39 | c
Average | 480.3333 | 0.013879 | 0.013879 | 0.027759 | Average | 36.3333 | 0.091743 | 0.018349 | 0.073394
|  | 2.776% | Voltage Balance in Percent |  |  |  | 9.174% | Current Balance in Percent
Note: this is a very close approximation used in MG 1-1993 NEMA Standard.
True unbalance is the negative sequence voltage or current with respect to positive sequance componets
Voltage Balance Percent
| 0 - 1.4 | Should be no issues
| 1.5 | Some submersible pumps will not run and trip
| 2 | Chillers and HVAC can trip at this level
| 2.5 | VSD (variable speed drives) and other control (typically HVAC)may trip
| 2.5 -3.0 | We need to do some investigation on Electrial system.
| 3 | ANSI recommend to stay below 3% voltage balance.
| > 3.0 | Phase monitor are typicaly set at this level to 5%
| 5 | NEMA derates motor up to this point.
5% is the top level for derating motors by NEMA.

## Sheet2
Vector analysis
cosine
| Volts | Phase Angle |  |  | Cosine | PI
A - N | 122 | 122 |  |  | -0.43837
B - N | 118 | 119 |  |  | -0.52992 | 3.1416
C - N | 118 | 119 |  |  | -0.52992
|  | 360 | THIS MUST BE 360
C - A | 203.5426 | Volts
A - B | 209.9177 | Volts
B - C | 206.4103 | Volts
Average | 206.6235 | 0.014911 | 0.015943 | 0.0010321
|  | 1.594% | Voltage Balance in Percent