## Three Phase Transformers
Three Phase Transformers
This is the voltage drop only on the transformer it does NOT include primary or secondary service drop
Input Blue
Transfomer Size | Impedance | nomal voltage | Start voltage | Votlage Drop | FLA
750 | 5.7 | 480 | 490 | 27.36 | 902.1098
Percent Loading | Voltage | Volage drop | Measured Loads | Percent Load
0 | 490 | 0 | Amps
10 | 487.264 | 2.736 | 760 | 84.25%
20 | 484.528 | 5.472 | 4000 | 443.4%
30 | 481.792 | 8.208
40 | 479.056 | 10.944
50 | 476.32 | 13.68
60 | 473.584 | 16.416
70 | 470.848 | 19.152
80 | 468.112 | 21.888
90 | 465.376 | 24.624
100 | 462.64 | 27.36
110 | 459.904 | 30.096
120 | 457.168 | 32.832
130 | 454.432 | 35.568
140 | 451.696 | 38.304
150 | 448.96 | 41.04
160 | 446.224 | 43.776
170 | 443.488 | 46.512
180 | 440.752 | 49.248
190 | 438.016 | 51.984
200 | 435.28 | 54.72
210 | 432.544 | 57.456
220 | 429.808 | 60.192
230 | 427.072 | 62.928
240 | 424.336 | 65.664

## Single Phase Transformers
Single Phase Transformers
This is the voltage drop only on the transformer it does NOT include primary or secondary service drop
Input Blue
Transfomer Size | Impedance | nomal voltage | Start voltage | Votlage Drop | FLA
750 | 5.7 | 240 | 490 | 13.68 | 3125
Percent Loading | Voltage | Volage drop | Measured Loads | Percent Load
0 | 490 | 0 | Amps
10 | 488.632 | 1.368 | 120 | 3.84%
20 | 487.264 | 2.736 | 298 | 9.536%
30 | 485.896 | 4.104
40 | 484.528 | 5.472
50 | 483.16 | 6.84
60 | 481.792 | 8.208
70 | 480.424 | 9.576
80 | 479.056 | 10.944
90 | 477.688 | 12.312
100 | 476.32 | 13.68
110 | 474.952 | 15.048
120 | 473.584 | 16.416
130 | 472.216 | 17.784
140 | 470.848 | 19.152
150 | 469.48 | 20.52
160 | 468.112 | 21.888
170 | 466.744 | 23.256
180 | 465.376 | 24.624
190 | 464.008 | 25.992
200 | 462.64 | 27.36
210 | 461.272 | 28.728
220 | 459.904 | 30.096
230 | 458.536 | 31.464
240 | 457.168 | 32.832

## Compatibility Report
Compatibility Report for Voltage Drop in Transformers.xls
Run on 3/12/2008 10:54
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 3